Device settings

Device tag	: Unit 1
Serial number	: L104AB04428

Name:	_____________________________________________

Department:	_____________________________________________

Company:	_____________________________________________

Address:	_____________________________________________

	_____________________________________________

	_____________________________________________

Telephone:	_____________________________________________

E-mail:	_____________________________________________

Device configured

_____________________________________________
Name, date, signature

Device configuration checked

_____________________________________________
Name, date, signature

Device configuration approved

_____________________________________________
Name, date, signature

Diagnostics

Diagnostics / Device information

Serial number	: L104AB04428
Order Code	: RSG35-D2DAAC1E1
Firmware Version	: 2.00.06
ENP version	: 2.02.00
ENP device name	: RSG35
Device name	: Ecograph T
Manufacturer ID	: 17
Manufacturer name	: Endress+Hauser
Firmware	: ENU000A

Diagnostics / Device information / Ethernet

MAC-Address	: 00-07-05-31-51-59
Service mode	: No

Diagnostics / Device information / Hardware

Power supply	: ENP00xA V1.20.02
Serial number	: 

Slot 1	: Universal inputs
Firmware Version	: ENA00xA V1.20.01
Serial number	: 3922B602

Slot 2	: Universal inputs
Firmware Version	: ENA00xA V1.20.01
Serial number	: 3922B5FE

Slot 3	: Universal inputs
Firmware Version	: ENA00xA V1.20.01
Serial number	: 3922B5F6

Diagnostics / Device information / Device options

Slot 1	: Universal inputs
Slot 2	: Universal inputs
Slot 3	: Universal inputs
Communication	: USB + Ethernet + RS232/485
Fieldbus	: Modbus Slave
Application	: Maths

Diagnostics / Device information / Memory information

Internal memory
Weeks	: 44
Days	: 2
Hours	: 12
SD card
Size	: 1 GB
Weeks	: 793
Days	: 6
Hours	: 16

Expert

Expert / System

Sprache/Language	: English
Device tag	: Unit 1
Temp. unit	: °C
Decimal separator	: Comma
Fault switching	: Relay 1
Keyboard layout	: Germany
Swap mouse buttons	: No
Paper size	: DIN A4
Lock operation	: never

Expert / System / Date/time setup

Date format	: DD.MM.YYYY
Time format	: 24 hour

Expert / System / Date/time setup / Date/time

UTC time zone	: +07:00: Bangkok

Expert / System / Date/time setup / NT/ST changeover

NT/ST changeover	: Automatic
NT/ST region	: Europe
Begin summer time
Occurrence	: Last
Day	: Sunday
Month	: March
Date	: 25.03.2018
Time	: 02:00
End summer time
Occurrence	: Last
Day	: Sunday
Month	: October
Date	: 29.10.2017
Time	: 03:00

Expert / System / Date/time setup / SNTP

SNTP	: No

Expert / System / Security

Protected by	: Open access
Lock hardware	: -----

Expert / System / External memory

Save as	: protected format
SD card
Memory build-up	: Stack memory
Warning at	: 90 %
Switches relay	: Not used
CSV settings
Separator for CSV	: Semicolon
Date/time	: Seperate columns
Operating time	: 0000h00:00

Expert / System / Messages

Acknowledging messages	: Do not save
Switches relay	: Not used

Expert / System / Screen saver

Screen saver	: Switched off
Alarm response	: Off on alarm

Expert / System / Device options

Slot 1	: Universal inputs
Slot 2	: Universal inputs
Slot 3	: Universal inputs
Communication	: USB + Ethernet + RS232/485
Fieldbus	: Modbus Slave
Application	: Maths

Expert / Inputs

Expert / Inputs / Universal inputs

Expert / Inputs / Universal inputs / Lev.Intake (1) (active)

Signal	: Current
Range	: 4-20 mA
Channel ident.	: Lev.Intake
Plot type	: Instantaneous value
Engineering unit	: m
Decimal point	: Two (X.YY)
Range start	: 0,00 m
Meas. range end	: 4,00 m
Zoom start	: 0,00 m
Zoom end	: 4,00 m
Damping	: 0,0 s

Expert / Inputs / Universal inputs / Lev.Intake (1) (active) / Meas.val. corrct.

Range start
Target value	: 0,00 m
Actual value	: 0,00 m
Meas. range end
Target value	: 4,00 m
Actual value	: 4,00 m

Expert / Inputs / Universal inputs / Lev.Intake (1) (active) / Totalization

Totalization	: No

Expert / Inputs / Universal inputs / Lev.Intake (1) (active) / Fault mode

NAMUR NE 43	: On
Time delay	: 0 s
On error	: Invalid calculation
Save event	: No

Expert / Inputs / Universal inputs / Flow RWT (2) (active)

Signal	: Current
Range	: 4-20 mA
Channel ident.	: Flow RWT
Plot type	: Average
Engineering unit	: l\s
Decimal point	: One (X.Y)
Range start	: 2000 l\s
Meas. range end	: 0,0 l\s
Zoom start	: 2000 l\s
Zoom end	: 0,0 l\s
Damping	: 0,0 s

Expert / Inputs / Universal inputs / Flow RWT (2) (active) / Meas.val. corrct.

Range start
Target value	: 2000 l\s
Actual value	: 2000 l\s
Meas. range end
Target value	: 0,0 l\s
Actual value	: 0,0 l\s

Expert / Inputs / Universal inputs / Flow RWT (2) (active) / Totalization (active)

Totalization	: Yes
Totalization base	: Second (s)
Unit	: m³
Low flow cut off	: 1,000000 l\s
Calc. factor	: 0,00100

Expert / Inputs / Universal inputs / Flow RWT (2) (active) / Fault mode

NAMUR NE 43	: On
Time delay	: 0 s
On error	: Invalid calculation
Save event	: No

Expert / Inputs / Universal inputs / Lev.Reservoir (3) (active)

Signal	: Current
Range	: 4-20 mA
Channel ident.	: Lev.Reservoir
Plot type	: Instantaneous value
Engineering unit	: m
Decimal point	: Two (X.YY)
Range start	: 0,00 m
Meas. range end	: 7,00 m
Zoom start	: 0,00 m
Zoom end	: 7,00 m
Damping	: 0,0 s

Expert / Inputs / Universal inputs / Lev.Reservoir (3) (active) / Meas.val. corrct.

Range start
Target value	: 0,00 m
Actual value	: 0,00 m
Meas. range end
Target value	: 7,00 m
Actual value	: 7,00 m

Expert / Inputs / Universal inputs / Lev.Reservoir (3) (active) / Totalization

Totalization	: No

Expert / Inputs / Universal inputs / Lev.Reservoir (3) (active) / Fault mode

NAMUR NE 43	: On
Time delay	: 0 s
On error	: Invalid calculation
Save event	: No

Expert / Inputs / Universal inputs / Flow Q2 (4) (active)

Signal	: Current
Range	: 4-20 mA
Channel ident.	: Flow Q2
Plot type	: Instantaneous value
Engineering unit	: l/s
Decimal point	: One (X.Y)
Range start	: 0,0 l/s
Meas. range end	: 2000,0 l/s
Zoom start	: 0,0 l/s
Zoom end	: 2000,0 l/s
Damping	: 0,0 s

Expert / Inputs / Universal inputs / Flow Q2 (4) (active) / Meas.val. corrct.

Range start
Target value	: 0 l/s
Actual value	: 0 l/s
Meas. range end
Target value	: 2000,0 l/s
Actual value	: 2000,0 l/s

Expert / Inputs / Universal inputs / Flow Q2 (4) (active) / Totalization (active)

Totalization	: Yes
Totalization base	: Second (s)
Unit	: m³
Low flow cut off	: 5,000000 l/s
Calc. factor	: 0,00100

Expert / Inputs / Universal inputs / Flow Q2 (4) (active) / Fault mode

NAMUR NE 43	: On
Time delay	: 0 s
On error	: Invalid calculation
Save event	: No

Expert / Inputs / Universal inputs / Flow Q1 (5) (active)

Signal	: Current
Range	: 4-20 mA
Channel ident.	: Flow Q1
Plot type	: Instantaneous value
Engineering unit	: l/s
Decimal point	: One (X.Y)
Range start	: 0 l/s
Meas. range end	: 1000 l/s
Zoom start	: 0 l/s
Zoom end	: 1000 l/s
Damping	: 0,0 s

Expert / Inputs / Universal inputs / Flow Q1 (5) (active) / Meas.val. corrct.

Range start
Target value	: 0 l/s
Actual value	: 0 l/s
Meas. range end
Target value	: 1000 l/s
Actual value	: 1000 l/s

Expert / Inputs / Universal inputs / Flow Q1 (5) (active) / Totalization (active)

Totalization	: Yes
Totalization base	: Second (s)
Unit	: m3
Low flow cut off	: 5 l/s
Calc. factor	: 0,001

Expert / Inputs / Universal inputs / Flow Q1 (5) (active) / Fault mode

NAMUR NE 43	: On
Time delay	: 0 s
On error	: Invalid calculation
Save event	: No

Expert / Inputs / Digital inputs

Expert / Inputs / Digital inputs / FWP-VII-01 (1) (active)

Function	: On/off event
Channel ident.	: FWP-VII-01
Time delay	: 0 s
Switches relay	: Not used
Description `H`	: on
Description `L`	: off
Save event	: Yes
Event Message	: Do not acknowledge
Event text L->H	: 
Event text H->L	: 
Record duration	: No

Expert / Inputs / Digital inputs / FWP-VII-02 (2) (active)

Function	: On/off event
Channel ident.	: FWP-VII-02
Time delay	: 0 s
Switches relay	: Not used
Description `H`	: on
Description `L`	: off
Save event	: Yes
Event Message	: Do not acknowledge
Event text L->H	: 
Event text H->L	: 
Record duration	: No

Expert / Inputs / Digital inputs / FWP-VII-03 (3) (active)

Function	: On/off event
Channel ident.	: FWP-VII-03
Time delay	: 0 s
Switches relay	: Not used
Description `H`	: on
Description `L`	: off
Save event	: Yes
Event Message	: Do not acknowledge
Event text L->H	: 
Event text H->L	: 
Record duration	: No

Expert / Inputs / Digital inputs / FWP-VII-04 (4) (active)

Function	: On/off event
Channel ident.	: FWP-VII-04
Time delay	: 0 s
Switches relay	: Not used
Description `H`	: on
Description `L`	: off
Save event	: Yes
Event Message	: Do not acknowledge
Event text L->H	: 
Event text H->L	: 
Record duration	: No

Expert / Inputs / Digital inputs / FWP-VII-05 (5) (active)

Function	: On/off event
Channel ident.	: FWP-VII-05
Time delay	: 0 s
Switches relay	: Not used
Description `H`	: on
Description `L`	: off
Save event	: Yes
Event Message	: Do not acknowledge
Event text L->H	: 
Event text H->L	: 
Record duration	: No

Expert / Inputs / Digital inputs / Digital input 6 (active)

Function	: Pulse counter
Channel ident.	: Digital 6
Engineering unit	: m³
Decimal point	: One (X.Y)
Pulse value	: 1 m³

Expert / Outputs

Expert / Outputs / Relay 1

Operating mode	: Closing
Identifier	: Relay 1

Expert / Outputs / Relay 2

Operating mode	: Closing
Identifier	: Relay 2

Expert / Outputs / Relay 3

Operating mode	: Closing
Identifier	: Relay 3

Expert / Outputs / Relay 4

Operating mode	: Closing
Identifier	: Relay 4

Expert / Outputs / Relay 5

Operating mode	: Closing
Identifier	: Relay 5

Expert / Outputs / Relay 6

Operating mode	: Closing
Identifier	: Relay 6

Expert / Communication

Timeout	: 0 s
Switches	: Not used
Timeout  fieldbus	: 10 s

Expert / Communication / Ethernet

MAC-Address	: 00-07-05-31-51-59
DHCP	: No
IP address	: 192.168.100.250
Subnetmask	: 255.255.255.000
Gateway	: 192.168.100.001
Domain Name System (DNS)	: 208.067.220.220
Disable port	: -----
Port	: 8000
OPC port	: 8002
Web server	: Yes

Expert / Communication / Ethernet / Configuration Web server

Port	: 80
HTTPS port	: 443
Setup	: Yes
Firmware update	: No
Remote control	: Yes
WebDAV server	: Yes

Expert / Communication / Ethernet / Configuration Web server / Authentication

Operator
ID	: operator
Password	: ************
Administrator
ID	: admin
Password	: ************
Service
ID	: service
Password	: ************

Expert / Communication / Serial interface

Type	: RS232
Protocol	: PC software
Baudrate	: 19200

Expert / Communication / Modbus Slave

Modbus	: Ethernet
Port	: 502

Expert / Application

Expert / Application / Maths

Expert / Application / Maths / Flow Q Total (1) (active)

Function	: Formula editor
Channel ident.	: Flow Q Total
Formula	: AI(1;5)+AI(1;4)
The result is	: Instantaneous value
Plot type	: Instantaneous value
Engineering unit	: l/s
Decimal point	: One (X.Y)
Zoom start	: 0 l/s
Zoom end	: 2000 l/s

Expert / Application / Maths / Flow Q Total (1) (active) / Totalization (active)

Totalization	: Yes
Totalization base	: Second (s)
Unit	: 
Low flow cut off	: 10 l/s
Calc. factor	: 0,001

Expert / Application / Maths / Flow Q Total (1) (active) / Fault mode

On error	: Invalid calculation

Expert / Application / Maths / Maths 2

Function	: Switched off

Expert / Application / Maths / Maths 3

Function	: Switched off

Expert / Application / Maths / Maths 4

Function	: Switched off

Expert / Application / Signal analysis

Analysis 1	: 1h
Analysis 2	: Daily analysis
Analysis 3	: Monthly analysis
Analysis 4	: Annual analysis
Synchron. time	: 08:00

Expert / Application / Limits

Expert / Application / Signal groups

Expert / Application / Signal groups / Analog (1) (active)

Identifier	: Analog
Save cycle	: 1min
Alarm cycle	: Off
Display blue	: Lev.Intake
Display	: Measured value/state
Display black	: Flow RWT
Display	: Measured value/state
Display red	: Lev.Reservoir
Display	: Measured value/state
Display green	: Flow Q1
Display	: Measured value/state
Display violet	: Flow Q2
Display	: Measured value/state
Display orange	: Flow Q Total
Display	: Measured value/state
Display cyan	: Switched off
Display brown	: Switched off
Grid divisions	: 10
Zoom	: Do not display

Expert / Application / Signal groups / STATUS POMPA (2) (active)

Identifier	: STATUS POMPA
Save cycle	: Off
Alarm cycle	: Off
Display blue	: FWP-VII-01
Display	: Measured value/state
Display black	: FWP-VII-02
Display	: Measured value/state
Display red	: FWP-VII-03
Display	: Measured value/state
Display green	: FWP-VII-04
Display	: Measured value/state
Display violet	: FWP-VII-05
Display	: Measured value/state
Display orange	: Switched off
Display cyan	: Switched off
Display brown	: Switched off
Grid divisions	: 10
Zoom	: Do not display

Expert / Application / Signal groups / Kubikasi (3) (active)

Identifier	: Kubikasi
Save cycle	: 1min
Alarm cycle	: 1min
Display blue	: Flow Q1
Display	: Everything
Display black	: Flow Q2
Display	: Everything
Display red	: Flow Q Total
Display	: Everything
Display green	: Switched off
Display violet	: Switched off
Display orange	: Switched off
Display cyan	: Switched off
Display brown	: Switched off
Grid divisions	: 10
Zoom	: Do not display

Expert / Application / Signal groups / Group 4

Identifier	: Group 4
Save cycle	: 1min
Alarm cycle	: 1min
Display blue	: Switched off
Display black	: Switched off
Display red	: Switched off
Display green	: Switched off
Display violet	: Switched off
Display orange	: Switched off
Display cyan	: Switched off
Display brown	: Switched off
Grid divisions	: 10
Zoom	: Do not display

Expert / Application / E-mail

SMTP host	: 
Server requires SSL	: No
Port	: 25
Sender	: 
User name	: 
Password	: **********************

Expert / Application / E-mail / E-mail addresses

E-mail address 1	: scadatirtanadi@gmail.com
E-mail address 2	: 
E-mail address 3	: 
E-mail address 4	: 
E-mail address 5	: 

Expert / Application / E-mail / Limit value violations

Recipient 1	: Not used
Recipient 2	: Not used

Expert / Application / E-mail / On/off messages

Recipient 1	: Not used
Recipient 2	: Not used

Expert / Application / E-mail / Errors (Fxxx)

Recipient 1	: Not used
Recipient 2	: Not used

Expert / Application / E-mail / Maintenance required (Mxxx)

Recipient 1	: Not used
Recipient 2	: Not used

Expert / Application / WebDAV client

Enable	: Yes
IP address	: 0.0.0.0
Port	: 80
User name	: scadatirtanadi
Password	: ********************
Directory	: 

Expert / Diagnostics

Expert / Diagnostics / Device information

Device tag	: Unit 1
Serial number	: L104AB04428
Order Code	: RSG35-D2DAAC1E1
Firmware Version	: 2.00.06
ENP version	: 2.02.00
ENP device name	: RSG35
Device name	: Ecograph T
Manufacturer ID	: 17
Manufacturer name	: Endress+Hauser
Firmware	: ENU000A

Expert / Diagnostics / Simulation

Operating mode	: Normal operation